## Cooling Tower System
Cooling Tower System
5 condensers ¦ return = 4,433,379 lb/hr @ 134.0 °F ¦ makeup = 428,996 lb/hr
PROCESS FLOW DIAGRAM
SYSTEM STREAMS (tags match the diagram)
# | Stream | lb/hr | GPM | °F
1 | Vapor from Evaporators & Pans | 190000
2 | Cool Water to Condensers (delivered blend) | 4243379.0674 | 8520.8415 | 88.4835
3 | Hot Water Return to Tower | 4433379.0674 | 8902.3676 | 134.0242
4 | Evaporated to Atmosphere | 175658.3142 | 352.7275
5 | Blowdown | 443337.9067 | 890.2368 | 134.0242
6 | Makeup Water | 428996.2209 | 861.4382 | 75
CONDENSER INVENTORY (5 condensers)
Condenser | Vapor (lb/hr) | Sat T (°F) | h_fg (BTU/lb) | Heat (MM BTU/hr) | Inj Water (lb/hr) | Inj Water (GPM) | Water Out (°F) | Total Out (lb/hr)
Set 1 Condenser | 60000 | 133.0828 | 1017.2286 | 61.0337 | 1368491.4142 | 2734.795 | 133.0828 | 1428491.4142
Set 2 Condenser | 35000 | 133.0828 | 1017.2286 | 35.603 | 798286.6583 | 1595.2971 | 133.0828 | 833286.6583
A Pans | 55000 | 143.3558 | 1011.2493 | 55.6187 | 1013602.6709 | 2025.5849 | 143.3558 | 1068602.6709
B Pans | 25000 | 133.0828 | 1017.2286 | 25.4307 | 570204.7559 | 1139.4979 | 133.0828 | 595204.7559
C Pans | 15000 | 119.6831 | 1024.9966 | 15.3749 | 492793.5681 | 984.7993 | 119.6831 | 507793.5681
Total | 190000 |  |  | 193.0611 | 4243379.0674 | 8479.9742 |  | 4433379.0674
Injection water supply temp | 88.4835 | °F
HOT WATER RETURN TO TOWER
Injection water (all condensers) | 4243379.0674 | lb/hr
Vapor condensed (all condensers) | 190000 | lb/hr
Total return | 4433379.0674 | lb/hr
Total return | 8902.3676 | GPM
Mixed return temperature | 134.0242 | °F
COOLING TOWER (blowdown 10.0%)
Hot water in | 4433379.0674 | lb/hr
Hot water temperature | 134.0242 | °F
Cool water temperature | 90 | °F
Blowdown | 443337.9067 | lb/hr
Blowdown | 890.2368 | GPM
Evaporated to atmosphere | 175658.3142 | lb/hr
Cool water from tower | 3814382.8465 | lb/hr
Cool water from tower | 7659.4033 | GPM
SYSTEM BALANCE
Cold water demand (condensers) | 4243379.0674 | lb/hr
Cool water available (tower) | 3814382.8465 | lb/hr
Makeup water required | 428996.2209 | lb/hr
Makeup water required | 861.4382 | GPM
Makeup water temperature | 75 | °F
Delivered injection water temp (cool + makeup blend) | 88.4835 | °F
Surplus (overflow) | 0 | lb/hr
Water in (vapor + makeup) | 618996.2209 | lb/hr
Water out (evap + BD + surplus) | 618996.2209 | lb/hr
Net (In - Out) | -1.1642e-10 | lb/hr